## PV
Description | code | type | cap_min | cap_max | unit | module_length_m | PV_th | PV_n | PV_noct | PV_Bref | PV_a0 | PV_a1 | PV_a2 | PV_a3 | PV_a4 | misc_losses | currency | a | b | c | d | e | LT_yr | O&M_% | IR_% | assumption
generic monocrystalline panel | PV1 | PV | 1 | 10000 | W | 1 | 0.002 | 0.16 | 43.5 | 0.0035 | 0.93582 | 0.054289 | 0.008677 | 0.000527 | -1.1e-05 | 0.1 | USD-2015 | 0 | 3.6383 | 1 | 0 | 0 | 20 | 1 | 5 | IR_%
generic monocrystalline panel | PV1 | PV | 10000 | 200000 | W | 1 | 0.002 | 0.16 | 43.5 | 0.0035 | 0.93582 | 0.054289 | 0.008677 | 0.000527 | -1.1e-05 | 0.1 | USD-2015 | 0 | 2.5988 | 1 | 0 | 0 | 20 | 1 | 5 | IR_%
generic monocrystalline panel | PV1 | PV | 200000 | 10000000000 | W | 1 | 0.002 | 0.16 | 43.5 | 0.0035 | 0.93582 | 0.054289 | 0.008677 | 0.000527 | -1.1e-05 | 0.1 | USD-2015 | 0 | 2.5988 | 1 | 0 | 0 | 20 | 1 | 5 | IR_%, capacity
generic polycrystalline panel | PV2 | PV | 1 | 10000 | W | 1 | 0.002 | 0.15 | 43.9 | 0.0044 | 0.91809 | 0.086257 | -0.024459 | 0.002816 | -0.000126 | 0.1 | USD-2015 | 0 | 3.6383 | 1 | 0 | 0 | 20 | 1 | 5 | IR_%
generic polycrystalline panel | PV2 | PV | 10000 | 200000 | W | 1 | 0.002 | 0.15 | 43.9 | 0.0044 | 0.91809 | 0.086257 | -0.024459 | 0.002816 | -0.000126 | 0.1 | USD-2015 | 0 | 2.5988 | 1 | 0 | 0 | 20 | 1 | 5 | IR_%
generic polycrystalline panel | PV2 | PV | 200000 | 10000000000 | W | 1 | 0.002 | 0.15 | 43.9 | 0.0044 | 0.91809 | 0.086257 | -0.024459 | 0.002816 | -0.000126 | 0.1 | USD-2015 | 0 | 2.5988 | 1 | 0 | 0 | 20 | 1 | 5 | IR_%, capacity
generic amorphous silicon panel | PV3 | PV | 1 | 10000 | W | 1 | 0.002 | 0.08 | 38.1 | 0.0026 | 1.1004 | -0.061423 | -0.0044273 | 0.0006315 | -1.9184e-05 | 0.1 | USD-2015 | 0 | 3.6383 | 1 | 0 | 0 | 20 | 1 | 5 | IR_%
generic amorphous silicon panel | PV3 | PV | 10000 | 200000 | W | 1 | 0.002 | 0.08 | 38.1 | 0.0026 | 1.1004 | -0.061423 | -0.0044273 | 0.0006315 | -1.9184e-05 | 0.1 | USD-2015 | 0 | 2.5988 | 1 | 0 | 0 | 20 | 1 | 5 | IR_%
generic amorphous silicon panel | PV3 | PV | 200000 | 10000000000 | W | 1 | 0.002 | 0.08 | 38.1 | 0.0026 | 1.1004 | -0.061423 | -0.0044273 | 0.0006315 | -1.9184e-05 | 0.1 | USD-2015 | 0 | 2.5988 | 1 | 0 | 0 | 20 | 1 | 5 | IR_%, capacity

## SC
Description | code | type | module_length_m | module_area_m2 | aperture_area_ratio | n0 | c1 | c2 | mB0_r | mB_max_r | mB_min_r | C_eff | t_max | IAM_d | dP1 | dP2 | dP3 | dP4 | Cp_fluid | cap_min | cap_max | unit | currency | a | b | c | d | e | LT_yr | O&M_% | IR_% | assumption
flat plate | SC1 | FP | 2 | 2.023 | 0.888 | 0.775 | 3.91 | 0.0081 | 57.98 | 86.97 | 28.99 | 8000 | 192 | 0.87 | 0 | 94.6324 | 150.2986 | 44.5329 | 3680 | 1 | 10000000000 | m2 | USD-2015 | 0 | 2130.9771 | 1 | 0 | 0 | 20 | 5 | 5 | IR_%
evacuated tube | SC2 | ET | 2 | 4.322 | 0.655 | 0.721 | 0.89 | 0.0199 | 88.2 | 147.12 | 33.1 | 39000 | 196 | 0.91 | 0 | 2825.9464 | 7771.3527 | 706.4866 | 3680 | 1 | 10000000000 | m2 | USD-2015 | 0 | 2130.9771 | 1 | 0 | 0 | 20 | 5 | 5 | IR_%

## PVT
Description | code | cap_min | cap_max | unit | currency | a | b | c | d | e | LT_yr | O&M_% | IR_% | assumption
generic PVT | PVT1 | 1 | 10000000000 | W | USD-2015 | 0 | 5.1975 | 1 | 0 | 0 | 20 | 1 | 5 | IR_%

## Boiler
Description | code | cap_min | cap_max | unit | currency | a | b | c | d | e | LT_yr | O&M_% | IR_% | assumption
condensing boiler | BO1 | 28000 | 90000 | W | USD-2015 | 22505.5432 | 0.30488 | 1 | 0 | 0 | 20 | 5 | 5
condensing boiler | BO1 | 90000 | 320000 | W | USD-2015 | 38913.5255 | 0.12195 | 1 | 0 | 0 | 20 | 5 | 5

## Furnace
Description | code | cap_min | cap_max | unit | currency | a | b | c | d | e | LT_yr | O&M_% | IR_% | assumption
furnace combined with ORC | FU1 | 1000000 | 5000000 | W | USD-2015 | 0 | 0.743 | 1 | 0 | 0 | 20 | 5 | 5
furnace combined with ORC | FU1 | 5000000 | 50000000 | W | USD-2015 | 0 | 0.743 | 1 | 0 | 0 | 20 | 5 | 5

## FC
Description | code | cap_min | cap_max | unit | currency | a | b | c | d | e | LT_yr | O&M_% | IR_% | Assumptions
solid oxide fuel cell | FC1 | 1000 | 10000 | W | USD-2015 | 0 | 13.7214 | 1 | 0 | 0 | 10 | 5 | 5
solid oxide fuel cell | FC1 | 10000 | 10000000000 | W | USD-2015 | 0 | 13.7214 | 1 | 0 | 0 | 10 | 5 | 5 | all

## CCGT
Description | code | cap_min | cap_max | unit | currency | a | b | c | d | e | LT_yr | O&M_% | IR_% | assumption
combined cycle gas turbine | CCGT1 | 1 | 10000000000 | W | USD-2015 | 0 | 555.8316 | 0.5967 | 0 | 0 | 25 | 3 | 6

## Chiller_configuration
CODE | SOURCE | COMPRESSOR | plf_a | plf_b | plf_c | q_a | q_b | q_c | q_d | q_e | q_f | REFERENCE
CH_T0 | WATER | SCREW | 0.33019 | 0.23554 | 0.46071 | 0.3327 | 0.0072912 | -0.00049938 | 0.01599 | -0.00028254 | 0.00052346 | https://comnet.org/index.php/382-chillers
CH_T1 | WATER | CENTRIFUGAL | 0.17149 | 0.5882 | 0.23737 | -0.29862 | 0.029961 | -0.00080125 | 0.017363 | -0.00032606 | 0.00063139 | https://comnet.org/index.php/382-chillers

## Chiller
Description | code | G_VALUE | cap_min | cap_max | unit | currency | a | b | c | d | e | LT_yr | O&M_% | IR_% | assumption
centralized chiller | CH1 | 0.47 | 1055000 | 14000000 | W | USD-2015 | 1568000 | 0.3049 | 1 | 0 | 0 | 25 | 5 | 3 | Fit based on RESCUE WP 2.4. Figure 18, 'cap_min': SSR530, 'cap_max': based on reported largest chiller: Haier Magnetic Bearing Centrifugal Chiller
vapor compression chiller | CH2 | 0.4 | 1 | 3500000 | W | USD-2015 | 12590.9091 | 0.14135 | 1 | 0 | 0 | 25 | 5 | 3 | IR_%
vapor compression chiller | CH3 | 0.4 | 1 | 3500000 | W | USD-2015 | 0 | 0.36063 | 1 | 0 | 0 | 25 | 5 | 3 | IR_%

## Absorption_chiller
Description | code | type | cap_min | cap_max | unit | currency | a | b | c | d | e | LT_yr | O&M_% | IR_% | assumption | s_e | r_e | s_g | r_g | a_e | e_e | a_g | e_g | m_cw | m_hw
LiBr single effect | ACH1 | single | 0 | 51150 | W | USD-2015 | 0 | 0.4395 | 1 | 0 | 0 | 25 | 5 | 5 | IR_% | 0.42 | 0.9 | 0.53 | -2.5 | -2.5 | 1.8 | -2.1 | 1.5 | 0.722 | 0.333
LiBr single effect | ACH2 | single | 51150 | 1176000 | W | USD-2015 | 0 | 0.4395 | 1 | 0 | 0 | 25 | 5 | 5 | IR_% | 68.12 | -3281.1 | 88.05 | -4216.1 | -1.45 | 1.75 | -1.45 | 1.75 | 81 | 33
LiBr double effect (dummy) | ACH3 | double | 0 | 58150 | W | USD-2015 | 0 | 0.5297 | 1 | 0 | 0 | 25 | 5 | 5 | IR_% | 0.42 | 0.9 | 0.53 | -2.5 | -2.5 | 1.8 | -2.1 | 1.5 | 0.722 | 0.333
LiBr double effect | ACH4 | double | 58150 | 1337450 | W | USD-2015 | 0 | 0.5297 | 1 | 0 | 0 | 25 | 5 | 5 | IR_% | 18.1 | -1350.5 | 12.54 | -917.3 | -2.46 | 4.38 | -2.46 | 4.38 | 68 | 14
LiBr triple effect | ACH5 | triple | 116300 | 1628200 | W | USD-2015 | 0 | 0.6424 | 1 | 0 | 0 | 25 | 5 | 5 | IR_% | 14.6 | -1171.7 | 7.05 | -504.2 | -2.14 | 3.29 | -2.14 | 3.29 | 62 | 10

## CT
Description | code | cap_min | cap_max | unit | currency | a | b | c | d | e | LT_yr | O&M_% | IR_% | assumption
centralized cooling tower | CT1 | 1 | 10000000 | W | USD-2015 | 1457.3 | 0.0161 | 1 | 0 | 0 | 20 | 5 | 3 | O&M_%

## HEX
Description | code | cap_min | cap_max | unit | Currency | a | b | c | d | e | a_p | b_p | c_p | d_p | e_p | LT_yr | O&M_% | IR_% | assumption
substation heat exchanger | HEX1 | 50000 | 80000 | W | USD-2015 | -346.1538 | 0.069647 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 5 | 5
substation heat exchanger | HEX1 | 80000 | 100000 | W | USD-2015 | 5197.5052 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 5 | 5
substation heat exchanger | HEX1 | 100000 | 10000000000 | W | USD-2015 | -3118.5031 | 0.08316 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 5 | 5
District substation heat exchanger | HEX2 | 0 | 500 | m^2 | USD-2015 | 3381 | 229.8 | 0 | 0 | 0 | 5056 | 319.9 | 0.4153 | -1271 | 0.006833 | 20 | 5 | 5 | Values under 1 and above 50 are assumptions, as no datasheet values are available in this area. a_p to e_p denote the pressure drop in Pa

## BH
Description | code | cap_min | cap_max | unit | currency | a | b | c | d | e | LT_yr | O&M_% | IR_% | assumption
borehole | BH1 | 1 | 10000000000 | W | USD-2015 | 0 | 47.4279 | 0.74 | 0 | 0 | 50 | 0 | 5

## HP
Description | code | cap_min | cap_max | unit | currency | a | b | c | d | e | LT_yr | O&M_% | IR_% | assumption
geothermal heat pump | HP1 | 1 | 10000000000 | W | USD-2015 | 0 | 197.1175 | 0.49 | 0 | 0 | 20 | 1 | 5
water-water heat pump | HP2 | 1000000 | 20000000 | W | USD-2015 | 0 | 9.8592 | 1 | 0 | -0.54715 | 25 | 5 | 6
water-water heat pump | HP2 | 20000000 | 20000000000000000 | W | USD-2015 | 0 | 9.8592 | 1 | 0 | -0.54715 | 25 | 5 | 6 | all

## Pump
Description | code | cap_min | cap_max | unit | currency | a | b | c | d | e | LT_yr | O&M_% | IR_% | assumption
generic pump | PU1 | 500 | 4000 | W | USD-2015 | 0 | 29.3139 | 0.5216 | 0 | 0 | 25 | 1 | 6 | LT_yr
generic pump | PU1 | 4000 | 37000 | W | USD-2015 | 0 | 4.323 | 0.7464 | 0 | 0 | 25 | 1 | 6 | LT_yr
generic pump | PU1 | 37000 | 375000 | W | USD-2015 | 0 | 1.0168 | 0.8873 | 0 | 0 | 25 | 1 | 6 | LT_yr
generic pump | PU1 | 375000 | 10000000000 | W | USD-2015 | 0 | 1.0168 | 0.8873 | 0 | 0 | 25 | 1 | 6 | all

## TES
Description | code | type | cap_min | cap_max | unit | currency | a | b | c | d | e | LT_yr | LT_mat_yr | O&M_% | IR_% | C_mat_% | T_PHCH_C | T_min_C | T_max_C | HL_kJkg | Rho_T_PHCH_kgm3 | Cp_kJkgK | n_ch | n_disch | assumption
short-term storage tank - water | TES1 | COOLING | 0 | 10000000000 | kWh | USD-2015 | 0 | 108 | 1 | 0 | 0 | 25 | 25 | 2 | 6 | 0 | 0 | 4 | 13 | 0 | 997 | 4.19 | 0.98 | 0.96 | cap_min, cap_max
short-term storage tank- ice | TES2 | COOLING | 0 | 10000000000 | kWh | USD-2015 | 0 | 117.9 | 1 | 0 | 0 | 25 | 25 | 2 | 6 | 4.8 | 0 | -6 | 7 | 334 | 917 | 2.11 | 0.98 | 0.96 | cap_min, cap_max
short-term storage tank - eutectic salt | TES3 | COOLING | 0 | 10000000000 | kWh | USD-2015 | 0 | 117.9 | 1 | 0 | 0 | 25 | 7 | 2 | 6 | 4.8 | 4 | 0 | 10 | 234 | 1600 | 2 | 0.98 | 0.96 | cap_min, cap_max
short-term storage tank - PEG400 | TES4 | COOLING | 0 | 10000000000 | kWh | USD-2015 | 0 | 156.3 | 1 | 0 | 0 | 25 | 7 | 2 | 6 | 27.3 | 5.4 | -1.5 | 10 | 105 | 1125 | 2.09 | 0.98 | 0.96 | cap_min, cap_max
short-term storage tank - Paraffin C14 | TES5 | COOLING | 0 | 10000000000 | kWh | USD-2015 | 0 | 141.5 | 1 | 0 | 0 | 25 | 7 | 2 | 6 | 19.7 | 5 | 2 | 10 | 230 | 760 | 2.14 | 0.98 | 0.96 | cap_min, cap_max

## CTES
Description | code | type | cap_min | cap_max | unit | currency | a | b | c | d | e | LT_yr | LT_mat_yr | O&M_% | IR_% | C_mat_% | T_PHCH_C | T_min_C | T_max_C | HL_kJkg | Rho_T_PHCH_kgm3 | Cp_kJkgK | n_ch | n_disch | assumption
short-term storage tank - water | TES1 | COOLING | 0 | 10000000000 | kWh | USD-2015 | 0 | 108 | 1 | 0 | 0 | 25 | 25 | 2 | 6 | 0 | 0 | 4 | 13 | 0 | 997 | 4.19 | 0.98 | 0.96 | cap_min, cap_max
short-term storage tank- ice | TES2 | COOLING | 0 | 10000000000 | kWh | USD-2015 | 0 | 117.9 | 1 | 0 | 0 | 25 | 25 | 2 | 6 | 4.8 | 0 | -0.5 | 0.5 | 334 | 917 | 2.11 | 0.98 | 0.96 | cap_min, cap_max
short-term storage tank - eutectic salt | TES3 | COOLING | 0 | 10000000000 | kWh | USD-2015 | 0 | 117.9 | 1 | 0 | 0 | 25 | 7 | 2 | 6 | 4.8 | 4 | 3.5 | 4.5 | 234 | 1600 | 2 | 0.98 | 0.96 | cap_min, cap_max
short-term storage tank - PEG400 | TES4 | COOLING | 0 | 10000000000 | kWh | USD-2015 | 0 | 156.3 | 1 | 0 | 0 | 25 | 7 | 2 | 6 | 27.3 | 5.4 | 4.9 | 5.9 | 105 | 1125 | 2.09 | 0.98 | 0.96 | cap_min, cap_max
short-term storage tank - Paraffin C14 | TES5 | COOLING | 0 | 10000000000 | kWh | USD-2015 | 0 | 141.5 | 1 | 0 | 0 | 25 | 7 | 2 | 6 | 19.7 | 5 | 4.5 | 5.5 | 230 | 760 | 2.14 | 0.98 | 0.96 | cap_min, cap_max