## DHW
Description | code | source_dhw | eff_dhw | PEN | CO2 | costs_kWh | reference
none | T0 | none | 0 | 0 | 0 | 0 | KBOB 2019
oil-fired boiler | T1 | OIL | 0.8 | 1.495 | 0.10189 | 0.2 | KBOB 2019
coal-fired furnace | T2 | COAL | 0.6 | 2.415 | 0.1725 | 0.2 | KBOB 2019
gas-fired boiler | T3 | NG | 0.8 | 1.403 | 0.099935 | 0.2 | KBOB 2019
electrical boiler | T4 | GRID | 0.9 | 2.722 | 0.042746 | - | KBOB 2019
wood-furnace | T5 | WOOD | 0.6 | 0.31893 | 0.016101 | 0.2 | KBOB 2019
heatpump - soil/water | T6 | GRID | 4 | 0.79925 | 0.01886 | - | KBOB 2019
solar collector | T7 | SC | 0.7 | 0.27715 | 0.01288 | 0 | KBOB 2019
heatpump - air/air (COP 2.7) | T8 | GRID | 2.7 | 1.1202 | 0.017591 | - | KBOB 2019
heatpump - water/water | T9 | GRID | 3 | 0.91425 | 0.020585 | - | KBOB 2019
district heating - gas-fired boiler | T10 | DH | 0.6 | 1.55 | 0.0869 | 0.08 | KBOB 2019
district heating - heatpump soil/water | T11 | DH | 0.6 | 1 | 0.0225 | 0.08 | KBOB 2019
district heating - oil | T12 | DH | 0.6 | 1.68 | 0.112 | 0.08 | KBOB 2019
district heating - other CHP | T13 | DH | 0.6 | 0.641 | 0.0377 | 0.08 | KBOB 2019
solar collector 30% + 70% gas-fired boiler | T15 | DH | 0.6 | 1.0652 | 0.073818 | 0.2 | KBOB 2019
district heating solar colector 60% + 40% gas-fired boiler | T16 | DH | 0.6 | 0.78629 | 0.042488 | 0.08 | KBOB 2019
district heating solar colector 60% + 30% heatpump - soil/water +10% gas-fired boiler | T17 | DH | 0.6 | 0.62129 | 0.023168 | 0.08 | KBOB 2019
district heating heat pump - water/water | T18 | DH | 0.6 | 1.2761 | 0.046404 | 0.08 | KBOB 2019
district heating Kerichtverbrennung CHP | T19 | DH | 0.6 | 0.0537 | 0.00094 | 0.08 | KBOB 2019
ETH network (district heating 43%, heat pump - water/water 28%, heat pump - waste heat 18%, heat recovery 11%) | T20 | DH | 0.6 | 0.44359 | 0.006993 | 0.08 | KBOB 2019
Note on A6: Jimeno Fonseca: All values + 15% of vertailverluste not included in th original factors. In order to trasnform from useful to final energy

## HEATING
Description | code | source_hs | eff_hs | PEN | CO2 | costs_kWh | reference
none | T0 | none | 0 | 0 | 0 | 0 | KBOB 2019
oil-fired boiler | T1 | OIL | 0.8 | 1.495 | 0.10189 | 0.2 | KBOB 2019
coal-fired furnace | T2 | COAL | 0.6 | 2.415 | 0.1725 | 0.2 | KBOB 2019
gas-fired boiler | T3 | NG | 0.8 | 1.403 | 0.099935 | 0.2 | KBOB 2019
electrical boiler | T4 | GRID | 0.9 | 2.722 | 0.042746 | - | KBOB 2019
wood-furnace | T5 | WOOD | 0.6 | 0.31893 | 0.016101 | 0.2 | KBOB 2019
heatpump - soil/water | T6 | GRID | 4 | 0.79925 | 0.01886 | - | KBOB 2019
solar collector | T7 | SC | 0.7 | 0.27715 | 0.01288 | 0 | KBOB 2019
heatpump - air/air | T8 | GRID | 2.7 | 1.1202 | 0.017591 | - | KBOB 2019
heatpump - water/water | T9 | GRID | 3 | 0.91425 | 0.020585 | - | KBOB 2019
district heating - gas-fired boiler | T10 | DH | 0.6 | 1.55 | 0.0869 | 0.08 | KBOB 2019
district heating - heatpump soil/water | T11 | DH | 0.6 | 1 | 0.0225 | 0.08 | KBOB 2019
district heating - oil | T12 | DH | 0.6 | 1.68 | 0.112 | 0.08 | KBOB 2019
district heating - other CHP | T13 | DH | 0.6 | 0.641 | 0.0377 | 0.08 | KBOB 2019
solar collector 30% + 70% gas-fired boiler | T15 | DH | 0.6 | 1.0652 | 0.073818 | 0.2 | KBOB 2019
district heating solar colector 60% + 40% gas-fired boiler | T16 | DH | 0.6 | 0.78629 | 0.042488 | 0.08 | KBOB 2019
district heating solar colector 60% + 30% heatpump - soil/water +10% gas-fired boiler | T17 | DH | 0.6 | 0.62129 | 0.023168 | 0.08 | KBOB 2019
district heating heat pump - water/water | T18 | DH | 0.6 | 1.2761 | 0.046404 | 0.08 | KBOB 2019
district heating Kerichtverbrennung CHP | T19 | DH | 0.6 | 0.0537 | 0.00094 | 0.08 | KBOB 2019
ETH network (district heating 43%, heat pump - water/water 28%, heat pump - waste heat 18%, heat recovery 11%) | T20 | DH | 0.6 | 0.44359 | 0.006993 | 0.08 | KBOB 2019
Note on A6: Jimeno Fonseca: All values + 15% of vertailverluste not included in th original factors. In order to trasnform from useful to final energy

## COOLING
Description | code | source_cs | eff_cs | PEN | CO2 | costs_kWh | reference
None | T0 | none | 0 | 0 | 0 | 0 | KBOB 2019
heatpump - air-air | T2 | GRID | 2.7 | 1.1202 | 0.017591 | - | KBOB 2019
heatpump - Water/water | T3 | GRID | 3 | 0.12488 | 0.0019563 | - | KBOB 2019
district cooling network - Lakewater/water | T4 | DC | 3.2 | 0.1561 | 0.0024453 | 0.074074 | KBOB 2019
district cooling network - air-air | T5 | DC | 2.8 | 0.5 | 0.062459 | 0.0675 | KBOB 2019

## ELECTRICITY
Description | code | source_el | eff_el | PEN | CO2 | costs_kWh | reference
None | T0 | 0 | 0 | 0 | 0 | 0 | KBOB 2019
Swiss consumer energy mix | T1 | GRID | 0.99 | 2.63 | 0.0413 | 0.2 | KBOB 2019
PV panel - monocrystalline roof top | T2 | PV | 0.99 | 0.278 | 0.0202 | 0 | KBOB 2019
Swiss consumer energy mix 70% + 30% PV | T4 | GRID | 0.99 | 1.9244 | 0.03497 | 0.2 | KBOB 2019
Singaporean consumer mix | T6 | GRID | 0.99 | 2 | 0.24984 | 0.27 | KBOB 2019